MATRIX DEVELOPMENT- A PREREQUISUTE FOR A SUCCESSFUL CLEANROOM DESIGN

By- Tim Loughran Managing Partner AdvanceTEC, LLC

Introduction. One of the most serious and common mistakes made in the design of cleanroom facilities is starting design before all the requirements have been identified. Properly executed programming and planning provide the most reliable foundation for a successful cleanroom design and construction project. Programming, a term utilized in the design community to make information gathering look more attractive to team participants, develops the body of information needed to identify, clarify, and prioritize the cleanroom requirements. The process of programming is the management of all preliminary project data assembled in a fashion to help determine design parameters of your new cleanroom facility. A cleanroom cannot accurately or responsibly be designed without assembling the following process requirements.

Equipment Database.  	This is the initial information that drives utilities, areas, and overall requirements.

Utility Requirement Summary. 	An analysis of services to each piece of the process equipment

Equipment Layout.	An analysis of cleanroom and other functional areas describing the areas needed for functioning and the additional areas required for support.

STEP 1

As we work through the process we’ll recognize the impact to design of the cleanroom, that not properly determining the most accurate requirements can have. and, more importantly, the impact to operation. Cleanroom facilities are typically intensive users of equipment and therefore are large consumers of utilities and process services.  The equipment database should be structured in a manner, which allows utility and raw material consumption data to be associated with each process tool and each piece of its associated auxiliary equipment. This information is recorded on an equipment information sheet. (see appendix “A”)

There are several avenues to develop reliable tool information data. We can acquire data from a similar facility that repeats the process in a new facility on another site. We can utilize equipment data from a pilot plant or R&D facility that will either be scaled-up or relocated and up-graded. We can tap into an engineering database of equipment maintained either by a consulting firm or by the manufacturing plant’s process engineers. We can research Operations and Maintenance manuals for the equipment. Or, we can utilize vendor supplied catalog data or sales brochures. In most cases it is a combination of the above and is compounded by process requirements that are not fully understood and equipment not yet fully sourced.

The data that needs to be collected should include all utilities and raw materials, which are required for normal process operations. In addition other items required to properly design the equipment integration into a cleanroom design are environmental parameters of operation, sizes, accessibility requirements, and support equipment requirements. Some semiconductor tools have as many as 7 or 8 support systems tethered to the process piece.

When collecting data, particularly from vendor sources, make sure that the data represents actual consumption data and not the nominal service capacity, which does not represent utility usage.  For example, many vendor data sheets list for the electrical utility requirements the electrical service, 20 amps at 120 volts, rather than the connected load, which may be only 300 watts or 2.5 amps at 120 volts.  Accumulated data errors such as this could dramatically distort demand requirements to the entire facility.

There may be as many individual ways to organize the data as there are people collecting it, which is why transferring the data into a standard format becomes paramount in determining if the information is complete and ultimately useful. The proper organization of the information allows for ease of transfer of such to the next step of the process.

STEP 2

We are now ready for the next step in determining our process requirements. This step has several purposes.

- To group equipment by process requirements and flow.

- To sort data by equipment to consider grouping of equipment with similar service requirements.

- To determine overall utility or raw material requirements to determine overall system demand.

- If process equipment is to be added in phases, the database will allow the engineers to study expansion options for central utility systems

Dependent upon your particular industry the summary of the accumulated equipment information sheets is known as a utility matrix, process utility summary, tool matrix, or utility requirement spreadsheet. (see appendix “B”)

Depending on the project’s size and the number of equipment information sheets, assembling this data can be a huge effort, although some design firms have sophisticated software programs that automatically link equipment information data sheet entries to a summary matrix.  Without assembling this data even experienced professionals will have difficulty guessing process requirements and will have no way of knowing whether the estimates are high or low.  Too low will lead to insufficient capacities and too high will result in expensive over building and inefficient operation which can be as problematic as under sizing. The alternate to this process is using “ruled of thumb” to size systems. Engineers are always seeking techniques to shorten their effort, and as a result, new rules of thumb are always being developed from existing facility data.  The problem with this modus operandi is that each facility has very custom requirements and these requirements cannot be generalized to other situations. Even when the sources are known, using rules of thumb may produce highly variable and often misleading results that cannot be verified; however, using rules of thumb as a litmus test to validate your results often serves as a valuable check and balance.

Once the utility and raw material data have been collected and accumulated in a summary spreadsheet the information can be utilized to properly determine process service requirements for the complete facility. We now have a means by which to properly assess items such as exhaust requirements, which in turn allows us to determine make up air requirements, which combined with humidity requirements determined from the equipment information sheets allows us to specify a make up air handler, which along with heat generation information of equipment and process cooling water needs allows us to properly size and specify a chiller.  The correct chiller size allows for the proper sizing of pumps and piping. You can see from this illustration the resultant cause and effect of improper information utilized in design efforts, and their resultant multiplying factors.

The data gathered to this point will provide the design effort with half of the information needed to successfully produce the appropriate cleanroom design.  Prior to the start of design, the project team should examine concepts applicable to work flow, flexibility, utility distribution, and other such issues. We now need to develop an equipment layout.  When assembling our tool data information we recorded equipment size and access requirements and grouped the equipment by work process. To develop the net area of the clean room, begin by developing the areas required for each piece of equipment, workstation and support area such as racks, storage, etc.  Access and maintenance space for equipment should be included with the equipment area requirement.  The total of these areas inside the cleanroom walls will produce the net cleanroom space. In addition to the cleanroom space, service corridors, mechanical rooms, utility rooms or basements will also be needed. We’ve determined the process services requirements for the equipment and can utilize that information to size support systems and their associated foot prints. It is very common for a cleanroom to require two to three times its area in available building space when support utility systems and services are incorporated.

We now have the cleanroom programmed and can accurately assess square footage requirements and begin to develop a budget. Until we have carried out this process we cannot accurately determine either item. In the realities of business the extent of this effort varies but in some type of form or format it must be completed prior to budgeting or assessing cleanroom requirements. If it hasn’t been extensively done or done at all, the value of the size and cost estimate you’re dealing with is subject to change.

Tim Loughran is Managing Partner for AdvanceTEC in Richmond, VA. AdvanceTEC is a design/build firm specializing in the construction of cleanrooms for the microelectronics, semiconductor, medical device, pharmaceutical, and food processing industries. Tim was formerly the Manager of Design/Build Services for Performance Contracting, Inc. and Division Manager for the Cleanroom Engineering Division of Cleanroom Products. He has nearly 20 years experience in the cleanroom industry and has published papers on numerous subjects including Clean Packaging Technology, Fan Filter Evaluation, Air Shower Performance, Retrofitting Cleanrooms, and Design/Build Cleanroom Specification and Proposal Evaluation. He is a frequent contributor to CleanRooms Magazine, a  speaker at the CleanRooms conferences, and former president of his local chapter of the IEST. Contact Tim at: TimL@advancetecllc.com Office Phone 804-378-1550. Office Fax 804-378-4055. The author wishes to acknowledge the support of Mark Hemingway and Tom Hansz in assembling the data for this article.